Technical Specification for UUTP CAT 6 CABLE-UL CMP

## 1. General Information

### 1.1 Cable Type

U/UTP CAT 6

### 1.2 Impedance

100 ohm

### 1.3 Certifications

UL, ETL, CE, CPR, RoHS

### 1.4 Length Options

100m, 305m, 500m, 500ft, 1000ft

### 1.5 Packing Options

Pull box, wooden spool, carton, pallet

### 1.6 Minimum Order Quantity (MOQ)

30KM

### 1.7 Delivery Time

Normally 25 working days (25 days after receiving the deposit)

### 1.8 Port of Loading

NINGBO, SHANGHAI

### 1.9 Payment Terms

T/T, L/C at sight, D/P at sight

2.1 Conductor

• Material: Solid Bare Copper

• Size: 23AWG

2.2 Pairs

4 Pairs

2.3 Insulation

• Thickness: 1.00±0.05 mm FEP

• Material: FEP

• Colors: Blue-White/Blue, Orange-White/Orange, Green-White/Green, Brown-White/Brown

2.4 Rip Cord

Kevlar

2.5 Spline/Cross Separator

FEP or LSZH CROSSWEB

2.6 Outer Jacket

• Material: Plenum PVC

• Wall Thickness: 0.0157" Nom(0.4mm)

• Outer Diameter (OD): 5.60±0.2mm

3. Standards Compliance

UL 444 & CSA C22.2 No.214 Communications Cables

4. Application Support

• 1000BASE-T, 1000BASE-TX, 100BASE-T, 100BASE-TX, 100VG-AnyLAN, ATM

• VoIP, ISDN, Token, 100MTPPDM, Analog and Data video, POE Type1,2,3,4

5. Electrical Characteristics

| Parameter | Specification |
| --- | --- |
| DC Resistance | ＜ 9.38 Ohms/100m @20 ℃ |
| DC Resistance Unbalance | 5% @ 20℃ |
| Mutual Capacitance | 5.6 nF/100m |
| Characteristic Impedance | 1 - 100 MHz : 100±15 Ohms; 101 - 250 MHz : 100±22 Ohms |
| Max Frequency | 250MHz |
| Capacitance Unbalance | 330 pF/100m |
| NVP (Nominal Velocity of Propagation) | ≥ 65% |
| Delay Skew | ≤ 44ns/100m |
| Working Voltage | Typically up to 48V |
| Rated Voltage (V RMS) | 300V |

- Transmission Performance (100m, 20±2℃)

| Frequency | Attenuation | NEXT (dB) | ACRF (dB) | PS.NEXT (dB) | PS.ACRF (dB) | RL (dB) | Delay (ns/100m) | Skew (ns/100m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MHz | dB | dB/100m | ns/100m | ns/100m | dB | dB | dB/100m | dB/100m |
| 1 | 2.0 | 74.3 | 67.8 | 72.3 | 64.8 | 20.0 | 570.0 | 45.0 |
| 4 | 3.8 | 65.3 | 55.8 | 63.3 | 52.8 | 23.0 | 552.0 |  |
| 8 | 5.3 | 60.8 | 49.7 | 58.8 | 46.7 | 24.5 | 546.7 |  |
| 10 | 6.0 | 59.3 | 47.8 | 57.3 | 44.8 | 25.0 | 545.4 |  |
| 16 | 7.6 | 56.2 | 43.7 | 54.2 | 40.7 | 25.0 | 543.0 |  |
| 20 | 8.5 | 54.8 | 41.8 | 52.8 | 38.8 | 25.0 | 542.0 |  |
| 25 | 9.5 | 53.3 | 39.8 | 51.3 | 36.8 | 24.3 | 541.2 |  |
| 31.25 | 10.7 | 51.9 | 37.9 | 49.9 | 34.9 | 23.6 | 540.4 |  |
| 62.5 | 15.4 | 47.4 | 31.9 | 45.4 | 28.9 | 21.5 | 538.6 |  |
| 100 | 19.8 | 44.3 | 27.8 | 42.3 | 24.8 | 20.1 | 537.6 |  |
| 200 | 29.0 | 39.8 | 21.8 | 37.8 | 18.8 | 18.0 | 536.5 |  |
| 250 | 32.8 | 38.3 | 19.8 | 36.3 | 16.8 | 17.3 | 536.3 |  |

7. Physical Properties

| Parameter | Specification |
| --- | --- |
| Pulling Tension (Max) | 25 lbs(110N) |
| Bend Radius (Min) | 4 Times the cable diameter |
| Operating Temperature | -20 to 75 ℃ （ -4 to 167 ℉） |