Technical Specification for MPO to MPO Fiber Trunk Cable (4*MPO-4*MPO)

## 1. Product Overview

This product is an MPO to MPO fiber trunk cable with a configuration of 4MPO-4MPO, designed for high-speed data transmission in optical communication systems. It provides reliable and efficient optical signal transmission through standardized MPO/MTP connectors, meeting the requirements of various high-bandwidth application scenarios.

## 2. Application Scope

The cable is suitable for use in scenarios that demand high-density and high-speed optical signal transmission, including but not limited to:

- Data centers (for interconnection between servers, storage devices, and network equipment)

- Telecommunication networks (backbone network transmission, metropolitan area network construction)

- Enterprise networks (large-scale office buildings, industrial parks, and campus network infrastructure)

- High-performance computing environments (connecting computing nodes in supercomputing centers)

## 3. Key Features

- Adopts standardized MPO/MTP connectors, supporting three connection methods: Method A, Method B, and Method C, ensuring compatibility with different network architectures.

- High transmission efficiency, capable of realizing low-loss and high-bandwidth optical signal transmission.

- Robust structural design, providing good mechanical protection and environmental adaptability to ensure stable operation in various working conditions.

- Flexible installation, suitable for different routing and deployment requirements in complex environments.

## 4. Installation Requirements

- Before installation, inspect the cable for any physical damage (such as scratches, breaks, or deformation of connectors) to ensure the product is intact.

- Confirm that the installation environment meets the operating conditions of the fiber cable (avoid extreme temperatures, humidity, strong electromagnetic interference, and sharp object extrusion).

- When connecting the MPO/MTP connectors, align them correctly according to the specified connection method (Method A, B, or C) to avoid forced insertion, which may cause damage to the connectors or fiber cores.

- Arrange the cable routing neatly, with appropriate bending radius (comply with general fiber cable installation standards) to prevent excessive bending that affects signal transmission.

- After installation, perform optical performance testing (such as insertion loss and return loss) to ensure the cable meets the application requirements.

## 5. Technical Specifications

### 5.1 Connector Specifications

- Connector type: MPO/MTP

- Number of connectors: 4 at each end (4MPO-4MPO configuration)

- Connection methods: Compatible with Method A, Method B, and Method C

- Insertion loss: Complies with relevant international and industry standards (typical value ≤ 0.3 dB, maximum value ≤ 0.5 dB)

- Return loss: ≥ 45 dB (for single-mode fiber); ≥ 35 dB (for multi-mode fiber)

- Connector material: High-quality engineering plastic, with good wear resistance and corrosion resistance

### 5.2 Fiber Core Specifications

- Fiber type: Optional single-mode fiber (SMF-28e or equivalent) or multi-mode fiber (OM3, OM4, or OM5)

- Fiber count: Consistent with the MPO/MTP connector configuration

- Attenuation coefficient:

- Single-mode fiber: ≤ 0.35 dB/km (at 1310 nm); ≤ 0.25 dB/km (at 1550 nm)

- Multi-mode fiber (OM4): ≤ 3.5 dB/km (at 850 nm); ≤ 1.5 dB/km (at 1300 nm)

- Chromatic dispersion: Meets the requirements of corresponding fiber type standards

### 5.3 Cable Structure Specifications

- Cable sheath material: LZSH (Low Smoke Zero Halogen) material, ensuring low smoke, non-toxic, and flame-retardant performance

- Sheath color: Customizable according to requirements (default color: black or gray)

- Cable diameter: Subject to dimensional diagram, consistent with the 4MPO-4MPO configuration

- Tensile strength: ≥ 1500 N (for long-term use); ≥ 3000 N (for short-term installation)

- Crush resistance: ≥ 1000 N/100 mm

- Operating temperature range: -40°C to +70°C

- Storage temperature range: -50°C to +85°C

### 5.4 Length Specifications

- Standard lengths: Customizable according to user requirements (common lengths include 1m, 2m, 3m, 5m, 10m, etc.)

- Length tolerance: ±0.5% of the specified length

## 6. Assembly Requirements

- The assembly process shall comply with strict quality control standards to ensure the consistency and reliability of product performance.

- Fiber splicing (if applicable) shall adopt precision splicing technology, with splicing loss meeting relevant standards.

- Connector polishing: Adopt PC (Physical Contact) or APC (Angled Physical Contact) polishing method to ensure low insertion loss and high return loss.

- After assembly, each cable undergoes 100% optical performance testing and visual inspection to eliminate defective products.

## 7. Dimensional Diagram

Refer to the product's dimensional diagram for specific structural dimensions (including cable diameter, connector size, connector spacing, etc.). The dimensional design shall be compatible with standard MPO/MTP connector installation interfaces and common deployment scenarios.